## Instructions
This program is a tool to evaluate the operational parameters of water treatment plant's
ability to comply with CT inactivation to meet the requirements of the
Surface Water Treatment Rules' and 'Ground Water Rule'
Instructions and Information:
All highlighted cells are available for data entry or data selection.
All other cells are fixed or provide results
The program will calculate the CT achieved and % log-inactivation compliance for Giardia, Virus, Cryptosporidium and Microcystin for each treatment segment and for the total of all segments (If multiple are used). It will also calculate the disinfectant residual required for each segment (and the required clearwell depth / pipeline length for those segments) to meet 100% CT compliance overall based on the other parameters remaining constant.
1. Enter the associated water treatment flow rates and required log inactivation for Giardia, Virus
Cryptosporidium or concentration of Microcystin as required for your treatment plant.
(Refer to the CT letter from ADH for inactivation requirements for the specific WTP.)
2. Enter or select data for all applicable segments (they do not have to be in actual order of treatment)
This includes the segment name, type and residual of the disinfectant, temperature, pH, volume,
baffle factor, associated flow rate.
3. If using a clearwell, enter one of the following in the right side of the Segment 1 data:
a) Volume (in gallons) of the clearwell per foot of depth.
b) Detention time (in minutes) per foot of clearwell depth.
c) Approved T10 minutes for the clearwell (based on a fixed depth)
NOTE: If condition b) is entered it will overide condition a), Condition c) will overide a) and b)
The program will calculate the minimum clearwell depth required to meet 100% CT compliance based on the other parameters remaining constant. (Options a & b only)
4. If using a pipeline, enter one of the following in the right side of the Segment 5 data:
a) Diameter (in inches) of the pipeline.
OR Select 'Volume' and enter the pipeline volume in gal.
OR Select 'Volume / ft' and enter the pipeline volume per foot of length in gal.
b) Detention time (in minutes) per foot of pipeline length.
c) Approved T10 minutes for the pipeline (based on a fixed length)
NOTE: If condition b) is entered it will overide condition a), Condition c) will overide a) and b)
The program will calculate the minimum pipeline length required to meet 100% CT compliance based on the other parameters remaining constant. (Options a & b only)
This program was developed by Lance A. Jones, P.E. with the Arkansas Department of Health - Engineering Section for use by water treatment plant operators, design engineers as well as regulatory and technical assistance personnel to evaluate the ability for disfinfection practices of water treatment plants to meet the CT requirements of the 'Surface Water Treatment Rule' and 'Ground Water Rule' as part of the Federal Safe Drinking Water Act.
This program utilizes the CT Tables for Chlorine, Chorine Dioxide, Ozone and Chloramines as published in the Safe Drinking Water Act (40 CFR part 141) and the Guidance Manuals for the Surface Water Treatment Rules.
Microcystin inactivation based on CT table located in the 'Draft White Paper on Cyanotoxin Treatment'
August 2015 by AWWA Ohio Section Technology Committee and Ohio EPA.
Macros are only needed for the automated data entry clear function. Program will work without macros but
will require manual clearing of data entry prior to a new calculation.
For Questions please contact the Engineering Section at 501-661-2623
Version 1.51 | 2018-04-17
Update History
Version 1.1 | 2010-01-04 | Corrected interpolation for Giardia CT between 1.6 and 1.8 Cl2 residual and revised required residual,
depth & length to value needed for combined 100% vs individual segment. Added comments to
clearwell and pipeline segments if multiple volume/time data entered. LAJ
Version 1.2 | 2010-01-06 | Corrected formating to report required residual, depth & length if only Giardia or Virus compliance
needed vs both. LAJ
Version 1.3 | 2010-01-27 | Incorporated Cryptosporidium CT for Chlorine Dioxide and Ozone. Allowed CT calculations for
temperatures above 25 C. LAJ
Version 1.4 | 2016-01-15 | Minor corrections in some calculation formulas. LAJ
Version 1.5 | 2016-09-01 | Incorporated Microcystin CT. Made some minor formating changes. LAJ
Version 1.51 | 2018-04-17 | Disabled macros version. LAJ

## CT Worksheet
| CT Compliance Calculation Worksheet |  |  |  |  | Enter PWS# and Plant Name | [5 empty] | Enter Date |  | SEGMENT LIST
|  |  | Enter PWS# and Plant Name | Enter Date
[8 empty] | Required Giardia |  |  | -log Inactivation
[8 empty] | Required Virus |  |  | -log Inactivation |  |  | Raw Water Line
Plant Flow | gpm |  |  |  | Residual & |  |  | Required Crypto |  |  | -log Inactivation |  |  | Rapid Mix
HS Flow | gpm |  |  |  | Depth/Length |  |  | Target Microcystin |  |  | -ug/l Inactivation |  |  | Flocculation
|  | CT Achieved |  |  | Needed for 100% CT | [6 empty] | Baffle Factor | Associated Flow Rate | Sedimentation
Clarifier
Clearwell | [6 empty] | Segment Name | [6 empty] | Filters
Minimum depth | [6 empty] | 1 | Clearwell |  |  | gal/ft |  |  | Filtered Water Line
Temp (C or F) | [13 empty] | Finished Water Line
Cl2 (free) | [8 empty] | OR enter time |  |  |  | min./ft | Other (enter name)
pH | [12 empty] | minutes
Segment 2 | [6 empty] | 2 |  |  |  | gal
Temp (C or F) | [13 empty] | TEMP LIST
Cl2 (free) | mg/l | [7 empty] | OR enter time |  |  |  | minutes | C
pH | [13 empty] | F
Segment 3 | [6 empty] | 3 |  |  |  | gal
Temp (C or F) | [13 empty] | FLOW LIST
Cl2 (free) | mg/l | [7 empty] | OR enter time |  |  |  | minutes | Plant
pH | [13 empty] | High Service
Both
Segment 4 | [6 empty] | 4 |  |  |  | gal |  |  | Backwash
Temp (C or F) | [13 empty] | HS + Backwash
Cl2 (free) | mg/l | [7 empty] | OR enter time |  |  |  | minutes
pH
Diameter
Pipeline | [6 empty] | 5 | Pipeline |  | Diameter |  |  |  | DISINFECTANT
Length | [10 empty] | in.
Temp (C or F) | [13 empty] | Cl2 (free)
Cl2 (free) | mg/l | [7 empty] | OR enter time |  |  |  | min./ft | Chlorine Dioxide
pH | [12 empty] | minutes | Ozone
Chloramine
Total CT
Achieved | [13 empty] | PIPELINE
1 | [13 empty] | Diameter
2 | [13 empty] | Volume
Volume / ft
Note on S3: Enter Required Giardia Inactivation (Must be greater than Zero and less than or equal to 3.0)
Note on S4: Enter Required Virus Inactivation (Must be greater than Zero and less than or equal to 4.0)
Note on C5: Enter maximum plant flow rate (gpm)
Note on S5: Enter Required Cryptosporidium Inactivation, if required, (Must be greater than Zero and less than or equal to 4.0)
Note on C6: Enter maximum high service flow rate (gpm)
Note on S6: Enter Target Microcystin concentration to Inactivate if required, (Must be greater than Zero and less than or equal to 100)
Note on C10: Enter minimum clearwell depth (ft) (If using gal/ft or min./ft values for segment 1)
Note on S10: Enter volume per foot of depth.
Note on U10: Enter the Baffle Factor for the segment (must be less than or equal to 1)
Note on C11: Enter minimum temperature
Note on B12: Select Disinfectant
Note on C12: Enter minimum disinfectant residual (mg/l)
Note on U12: OPTIONAL: Enter time per ft of depth in lieu of volume.
Note on C13: Enter maximum pH
Note on U13: OPTIONAL: Enter T10 time in lieu of volume or time per ft of depth
Note on S15: Enter Volume of segment (gal)
Note on U15: Enter the Baffle Factor for the segment (must be less than or equal to 1)
Note on C16: Enter minimum temperature
Note on B17: Select Disinfectant
Note on C17: Enter minimum disinfectant residual (mg/l)
Note on U17: OPTIONAL: Enter T10 time in lieu of volume
Note on C18: Enter maximum pH
Note on S20: Enter Volume of segment (gal)
Note on U20: Enter the Baffle Factor for the segment (must be less than or equal to 1)
Note on C21: Enter minimum temperature
Note on B22: Select Disinfectant
Note on C22: Enter minimum disinfectant residual (mg/l)
Note on U22: OPTIONAL: Enter T10 time in lieu of volume
Note on C23: Enter maximum pH
Note on S25: Enter Volume of segment (gal)
Note on U25: Enter the Baffle Factor for the segment (must be less than or equal to 1)
Note on C26: Enter minimum temperature
Note on B27: Select Disinfectant
Note on C27: Enter minimum disinfectant residual (mg/l)
Note on U27: OPTIONAL: Enter T10 time in lieu of volume
Note on C28: Enter maximum pH
Note on S30: Select: Diameter OR Volume per foot OR Volume
Note on C31: Enter minimum pipeline length (ft) (If using diameter,volume/ft or min./ft values for segment 5)
Note on Q31: Enter pipe description ie: Raw, Filtered, Finished, etc.
Note on S31: Enter: Diameter of pipe in inches Or Volume in gallons Or Volume per foot in inches
Note on U31: Enter the Baffle Factor for the segment (must be less than or equal to 1)
Note on C32: Enter minimum temperature
Note on B33: Select Disinfectant
Note on C33: Enter minimum disinfectant residual (mg/l)
Note on U33: OPTIONAL: Enter time per ft of length in lieu of volume.
Note on C34: Enter maximum pH
Note on U34: OPTIONAL: Enter T10 time in lieu of volume or time per ft of length

## Calculations (hidden)
CT Calculations | [5 empty] | Giardia |  | Virus |  |  |  | Crypto |  |  |  | Microcystin |  |  |  | Required Cl2 for 100% Giardia CT | [25 empty] | Residuals needed for 100% | [5 empty] | Seg 1 | Seg 2 | Seg 3 | Seg 4 | Seg 5 |  |  |  |  | Seg 1 | Seg 2 | Seg 3 | Seg 4 | Seg 5 |  |  |  |  | Seg 1 | Seg 2 | Seg 3 | Seg 4 | Seg 5
Segment | Flow Rate | Volume | T10 Time | CT achieved | Temp. | CT required | Percent | CT required |  | Percent |  | CT required |  | Percent |  | CT required | Percent |  |  | Seg 1 | Seg 2 | Seg 3 | Seg 4 | Seg 5 | # | Cl2 | CTrS1 | CTcS1 | CTrS2 | CTcS2 | CTrS3 | CTcS3 | CTrS4 | CTcS4 | CTrS5 | CTcS5 |  |  | Seg 1 | Seg 2 | Seg 3 | Seg 4 | Seg 5 |  |  | Micro- |  | Giardia
| gpm | gallons | min | min-mg/l | C | min-mg/l | CT achieved | min-mg/l |  | CT achieved |  | min-mg/l |  | CT achieved |  | min-mg/l | CT achieved | [7 empty] | 1 | 0.4 | [11 empty] | CL2r1 | [7 empty] | cystins | Crypto | & Virus | Actual |  | Required ClO for 100% Giardia CT | [8 empty] | Required Ozone for 100% Giardia CT | [8 empty] | Required Chloramine for 100% Giardia CT
Clearwell | [24 empty] | 2 | 0.6 | [11 empty] | CL2ra | [12 empty] | clocalc | [8 empty] | o3calc | [8 empty] | clnhcalc
[6 empty] | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 | [8 empty] | 3 | 0.8 | [11 empty] | CL2rb | [12 empty] | ClORg | [8 empty] | O3Rg | [8 empty] | ClNHRg | [9 empty] | Required Cl2 for 100% Microcystin CT per Segment | [8 empty] | Required Ozone for 100% Microcystin CT
Segment 2 | [24 empty] | 4 | 1 | [25 empty] | mg/l | mg/l | mg/l | mg/l | mg/l |  |  |  |  | mg/l | mg/l | mg/l | mg/l | mg/l |  |  |  |  | mg/l | mg/l | mg/l | mg/l | mg/l |  |  |  |  | cl2calc | [8 empty] | o3calc
[25 empty] | 5 | 1.2 | [11 empty] | # | [40 empty] | CL2Rm | [8 empty] | O3Rm
Segment 3 | [24 empty] | 6 | 1.4 | [11 empty] | CTra | [12 empty] | Required ClO for 100% Virus CT | [8 empty] | Required Ozone for 100% Virus CT | [8 empty] | Required Chloramine for 100% Virus CT | [10 empty] | mg/l | mg/l | mg/l | mg/l | mg/l |  |  |  |  | mg/l | mg/l | mg/l | mg/l | mg/l
[25 empty] | 7 | 1.6 | [11 empty] | TTrb | [12 empty] | clocalc | [8 empty] | o3calc | [8 empty] | clnhcalc
Segment 4 | [24 empty] | 8 | 1.8 | [11 empty] | Required Cl2 for 100% Giardia CT | [12 empty] | ClORv | [8 empty] | O3Rv | [8 empty] | ClNHRv
[25 empty] | 9 | 2 | [11 empty] | cl2calc | [13 empty] | mg/l | mg/l | mg/l | mg/l | mg/l |  |  |  |  | mg/l | mg/l | mg/l | mg/l | mg/l |  |  |  |  | mg/l | mg/l | mg/l | mg/l | mg/l
Pipeline | [24 empty] | 10 | 2.2 | [11 empty] | CL2Rg
[6 empty] | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 | [8 empty] | 11 | 2.4 | [12 empty] | mg/l | mg/l | mg/l | mg/l | mg/l | [7 empty] | Required ClO for 100% Crypto CT | [8 empty] | Required Ozone for 100% Crypto CT
Depth of clearwell needed for 100% in S1 | [5 empty] | Total CT | [18 empty] | 12 | 2.6 | [11 empty] | Required Cl2 for 100% Virus CT per Segment | [12 empty] | clocalc | [8 empty] | o3calc
[5 empty] | ft | Achieved | [18 empty] | 13 | 2.8 | [11 empty] | cl2calc | [12 empty] | ClORc | [8 empty] | O3Rc
[25 empty] | 14 | 3 | [11 empty] | CL2Rv | [13 empty] | mg/l | mg/l | mg/l | mg/l | mg/l |  |  |  |  | mg/l | mg/l | mg/l | mg/l | mg/l
Lenth of pipe needed for 100% in S5 | [38 empty] | mg/l | mg/l | mg/l | mg/l | mg/l
ft
| % Below |  |  | Segment 1 | Giardia CT Cl2 (free) |  |  | Segment 1 |  | CT Values |  | Interpolate pH |  | log-I | Temp | Cl2 |  |  | Segment 1 Required Cl2 for 100% Giardia CT | [8 empty] | Interpolate pH |  |  |  |  | Temperature |  | Log I | [42 empty] | % Below |  | Segment 1 | Microcystin CT Cl2 (free) |  |  |  | Interpolate pH |  | ug/l | Temp |  | Segment 1 Microcystin CT Ozone
Log G category 1 | 0% |  |  | Clearwell |  |  |  | Clearwell | [10 empty] | CT Table |  | CT Table |  | CT Table |  | CT Table | [15 empty] | Segment 1 Virus CT Cl2 (free) | [12 empty] | Segment 1 CT Chlorine Dioxide | [8 empty] | Segment 1 CT Ozone | [8 empty] | Segment 1 CT Chloramine |  |  |  |  | Log G category 1 | 0% |  | Clearwell
Log G category 2 | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -log |  |  |  | CL2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | -log |  |  | % Below |  |  | Clearwell |  |  |  | Interpolate pH |  | log-I |  | Temp |  | % Below |  |  | Clearwell | [5 empty] | % Below |  |  | Clearwell | [5 empty] | % Below |  |  | Clearwell |  |  |  |  | Log G category 2
pH category 1 S1 | 0% | [6 empty] | CT Table |  | CT Table | [7 empty] | 0.4 | [18 empty] | Log V category 1 | 0% | [11 empty] | ClOLog G category 1 | 0% | [5 empty] | Interpolate |  | O3Log G category 1 | 0% | [5 empty] | Interpolate |  | ClALog G category 1 | 0% | [5 empty] | Interpolate |  | pH category 1 S1 | 0% |  |  | Virus CT Table | [9 empty] | CT req.
pH category 2 S1 | [6 empty] | #N/A | [10 empty] | 0.6 | [18 empty] | Log V category 2 |  |  |  | Virus CT Table | [8 empty] | ClOLog G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | O3Log G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | ClALog G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | pH category 2 S1 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ug/l
Temp catergory 1 S1 | 0% | [5 empty] | #N/A | [10 empty] | 0.8 | [18 empty] | pH V category 1 S1 | 0% |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -log |  |  | ClOLog V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | O3Log V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | ClALog V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | Temp catergory 1 S1 | 0% |  | #N/A
Temp catergory 2 S1 | [7 empty] | #N/A |  | #N/A |  | #N/A | [5 empty] | 1 | [18 empty] | pH V category 2 S1 |  |  | #N/A | [9 empty] | ClOLog V category 2 |  |  | #N/A | [5 empty] | O3Log V category 2 |  |  | #N/A | [5 empty] | ClALog V category 2 |  |  | #N/A | [5 empty] | Temp catergory 2 S1 |  |  | #N/A
Cl2 catergory 1 S1 | [17 empty] | 1.2 | [18 empty] | Temp catergory 1 S1 | 0% |  | #N/A | [12 empty] | #N/A | [8 empty] | #N/A | [8 empty] | #N/A | [13 empty] | pH
Cl2 catergory 2 S1 | [7 empty] | CT Table |  | CT Table | [7 empty] | 1.4 | [18 empty] | Temp catergory 2 S1 | [7 empty] | pH |  |  |  |  | Temp catergory 1 S1 | 0% | [7 empty] | Temp catergory 1 S1 | 0% | [7 empty] | Temp catergory 1 S1 | 0%
Cl2a S1 | [6 empty] | #N/A | [10 empty] | 1.6 | [31 empty] | Temp catergory 2 S1 |  |  |  | Virus CT Table |  |  |  | Temp | Temp catergory 2 S1 |  |  |  | Virus CT Table |  |  |  | Temp | Temp catergory 2 S1
Cl2b S1 | [6 empty] | #N/A | [10 empty] | 1.8 | [35 empty] | #N/A | #N/A |  | -log | [5 empty] | #N/A | #N/A |  | -log | [8 empty] | Interpolate
|  |  |  | Table # |  |  |  | #N/A |  | #N/A |  | #N/A | [5 empty] | 2 | [18 empty] | V Column Index 1 | [12 empty] | ClOLog C category 1 | 0% |  | #N/A | [5 empty] | O3Log C category 1 | 0% |  | #N/A | [9 empty] | Virus CT Table |  |  |  | Temp
Column Index 1 | [17 empty] | 2.2 | [18 empty] | V Column Index 2 | [12 empty] | ClOLog C category 2 |  |  | #N/A | [5 empty] | O3Log C category 2 |  |  | #N/A | [9 empty] | #N/A | #N/A |  | -log |  | V Column Index 1
Column Index 2 | [17 empty] | 2.4 | [31 empty] | Temp catergory C1 S1 | [8 empty] | Temp catergory C1 S1 | [11 empty] | #N/A | [5 empty] | V Column Index 2
Column Index 3 | [17 empty] | 2.6 | [31 empty] | Temp catergory C2 S1 |  |  |  | Crypto CT Table |  |  |  | Temp | Temp catergory C2 S1 |  |  |  | Crypto CT Table |  |  |  | Temp |  |  |  | #N/A
Column Index 4 | [17 empty] | 2.8 | [31 empty] | Temp cat a |  |  |  | #N/A | #N/A |  | -log |  | Temp cat a |  |  |  | #N/A | #N/A |  | -log
[18 empty] | 3 | [31 empty] | Temp cat b |  |  | #N/A | [5 empty] | Temp cat b |  |  | #N/A
[19 empty] | #N/A |  | #N/A |  | #N/A |  | #N/A |  |  | #N/A |  | #N/A |  |  | pH , | [19 empty] | #N/A | [8 empty] | #N/A
| % Below |  |  | Segment 2 | Giardia CT Cl2 (free) |  |  | Segment 2 |  | CT Values |  | Interpolate pH |  | log-I | Temp | Cl2 |  |  | Segment 2 Required Cl2 for 100% Giardia CT | [8 empty] | Interpolate pH |  |  |  |  | Temperature |  | Log I | [42 empty] | % Below |  | Segment 2 | Microcystin CT Cl2 (free) |  |  |  | Interpolate pH |  | ug/l | Temp |  | Segment 2 Microcystin CT Ozone
Log G category 1 | 0% |  |  | Segment 2 |  |  |  | Segment 2 | [10 empty] | CT Table |  | CT Table |  | CT Table |  | CT Table | [15 empty] | Segment 2 Virus CT Cl2 (free) | [12 empty] | Segment 2 CT Chlorine Dioxide | [8 empty] | Segment 2 CT Ozone | [8 empty] | Segment 2 CT Chloramine |  |  |  |  | Log G category 1 | 0% |  | 0
Log G category 2 | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -log |  | mg/l |  | CL2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | -log |  |  | % Below |  |  | Segment 2 |  |  |  | Interpolate pH |  | log-I |  | Temp |  | % Below |  |  | Segment 2 | [5 empty] | % Below |  |  | Segment 2 | [5 empty] | % Below |  |  | Segment 2 |  |  |  |  | Log G category 2
pH category 1 S2 | 0% | [6 empty] | CT Table |  | CT Table | [7 empty] | 0.4 | [18 empty] | Log V category 1 | 0% | [11 empty] | ClOLog G category 1 | 0% | [5 empty] | Interpolate |  | O3Log G category 1 | 0% | [5 empty] | Interpolate |  | ClALog G category 1 | 0% | [5 empty] | Interpolate |  | pH category 1 S1 | 0% |  |  | Virus CT Table | [9 empty] | CT req.
pH category 2 S2 | [6 empty] | #N/A | [10 empty] | 0.6 | [18 empty] | Log V category 2 |  |  |  | Virus CT Table | [8 empty] | ClOLog G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | O3Log G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | ClALog G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | pH category 2 S1 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ug/l
Temp catergory 1 S2 | 0% | [5 empty] | #N/A | [10 empty] | 0.8 | [18 empty] | pH V category 1 S2 | 0% |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -log |  |  | ClOLog V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | O3Log V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | ClALog V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | Temp catergory 1 S1 | 0% |  | #N/A
Temp catergory 2 S2 | [7 empty] | #N/A |  | #N/A |  | #N/A | [5 empty] | 1 | [18 empty] | pH V category 2 S2 |  |  | #N/A | [9 empty] | ClOLog V category 2 |  |  | #N/A | [5 empty] | O3Log V category 2 |  |  | #N/A | [5 empty] | ClALog V category 2 |  |  | #N/A | [5 empty] | Temp catergory 2 S1 |  |  | #N/A
Cl2 catergory 1 S2 | [17 empty] | 1.2 | [18 empty] | Temp catergory 1 S2 | 0% |  | #N/A | [12 empty] | #N/A | [8 empty] | #N/A | [8 empty] | #N/A | [13 empty] | pH
Cl2 catergory 2 S2 | [7 empty] | CT Table |  | CT Table | [7 empty] | 1.4 | [18 empty] | Temp catergory 2 S2 | [7 empty] | pH |  |  |  |  | Temp catergory 1 S2 | 0% | [7 empty] | Temp catergory 1 S2 | 0% | [7 empty] | Temp catergory 1 S2 | 0%
Cl2a S2 | [6 empty] | #N/A | [10 empty] | 1.6 | [31 empty] | Temp catergory 2 S2 |  |  |  | Virus CT Table |  |  |  | Temp | Temp catergory 2 S2 |  |  |  | Virus CT Table |  |  |  | Temp | Temp catergory 2 S2
Cl2b S2 | [6 empty] | #N/A | [10 empty] | 1.8 | [35 empty] | #N/A | #N/A |  | -log | [5 empty] | #N/A | #N/A |  | -log | [8 empty] | Interpolate
|  |  |  | Table # |  |  |  | #N/A |  | #N/A |  | #N/A | [5 empty] | 2 | [18 empty] | V Column Index 1 | [12 empty] | ClOLog C category 1 | 0% |  | #N/A | [5 empty] | O3Log C category 1 | 0% |  | #N/A | [9 empty] | Virus CT Table |  |  |  | Temp
Column Index 1 | [17 empty] | 2.2 | [18 empty] | V Column Index 2 | [12 empty] | ClOLog C category 2 |  |  | #N/A | [5 empty] | O3Log C category 2 |  |  | #N/A | [9 empty] | #N/A | #N/A |  | -log |  | V Column Index 1
Column Index 2 | [17 empty] | 2.4 | [31 empty] | Temp catergory C1 S1 | [8 empty] | Temp catergory C1 S1 | [11 empty] | #N/A | [5 empty] | V Column Index 2
Column Index 3 | [17 empty] | 2.6 | [31 empty] | Temp catergory C2 S1 |  |  |  | Crypto CT Table |  |  |  | Temp | Temp catergory C2 S1 |  |  |  | Crypto CT Table |  |  |  | Temp |  |  |  | #N/A
Column Index 4 | [17 empty] | 2.8 | [31 empty] | Temp cat a |  |  |  | #N/A | #N/A |  | -log |  | Temp cat a |  |  |  | #N/A | #N/A |  | -log
[18 empty] | 3 | [31 empty] | Temp cat b |  |  | #N/A | [5 empty] | Temp cat b |  |  | #N/A
[19 empty] | #N/A |  | #N/A |  | #N/A |  | #N/A |  |  | #N/A |  | #N/A |  |  | pH , | [19 empty] | #N/A | [8 empty] | #N/A
| % Below |  |  | Segment 3 | Giardia CT Cl2 (free) |  |  | Segment 3 |  | CT Values |  | Interpolate pH |  | log-I | Temp | Cl2 |  |  | Segment 3 Required Cl2 for 100% Giardia CT | [8 empty] | Interpolate pH |  |  |  |  | Temperature |  | Log I | [42 empty] | % Below |  | Segment 3 | Microcystin CT Cl2 (free) |  |  |  | Interpolate pH |  | ug/l | Temp |  | Segment 3 Microcystin CT Ozone
Log G category 1 | 0% |  |  | Segment 3 |  |  |  | Segment 3 | [10 empty] | CT Table |  | CT Table |  | CT Table |  | CT Table | [15 empty] | Segment 3 Virus CT Cl2 (free) | [12 empty] | Segment 3 CT Chlorine Dioxide | [8 empty] | Segment 3 CT Ozone | [8 empty] | Segment 3 CT Chloramine |  |  |  |  | Log G category 1 | 0% |  | 0
Log G category 2 | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -log |  | mg/l |  | CL2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | -log |  |  | % Below |  |  | Segment 3 |  |  |  | Interpolate pH |  | log-I |  | Temp |  | % Below |  |  | Segment 3 | [5 empty] | % Below |  |  | Segment 3 | [5 empty] | % Below |  |  | Segment 3 |  |  |  |  | Log G category 2
pH category 1 S3 | 0% | [6 empty] | CT Table |  | CT Table | [7 empty] | 0.4 | [18 empty] | Log V category 1 | 0% | [11 empty] | ClOLog G category 1 | 0% | [5 empty] | Interpolate |  | O3Log G category 1 | 0% | [5 empty] | Interpolate |  | ClALog G category 1 | 0% | [5 empty] | Interpolate |  | pH category 1 S1 | 0% |  |  | Virus CT Table | [9 empty] | CT req.
pH category 2 S3 | [6 empty] | #N/A | [10 empty] | 0.6 | [18 empty] | Log V category 2 |  |  |  | Virus CT Table | [8 empty] | ClOLog G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | O3Log G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | ClALog G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | pH category 2 S1 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ug/l
Temp catergory 1 S3 | 0% | [5 empty] | #N/A | [10 empty] | 0.8 | [18 empty] | pH V category 1 S3 | 0% |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -log |  |  | ClOLog V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | O3Log V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | ClALog V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | Temp catergory 1 S1 | 0% |  | #N/A
Temp catergory 2 S3 | [7 empty] | #N/A |  | #N/A |  | #N/A | [5 empty] | 1 | [18 empty] | pH V category 2 S3 |  |  | #N/A | [9 empty] | ClOLog V category 2 |  |  | #N/A | [5 empty] | O3Log V category 2 |  |  | #N/A | [5 empty] | ClALog V category 2 |  |  | #N/A | [5 empty] | Temp catergory 2 S1 |  |  | #N/A
Cl2 catergory 1 S3 | [17 empty] | 1.2 | [18 empty] | Temp catergory 1 S3 | 0% |  | #N/A | [12 empty] | #N/A | [8 empty] | #N/A | [8 empty] | #N/A | [13 empty] | pH
Cl2 catergory 2 S3 | [7 empty] | CT Table |  | CT Table | [7 empty] | 1.4 | [18 empty] | Temp catergory 2 S3 | [7 empty] | pH |  |  |  |  | Temp catergory 1 S3 | 0% | [7 empty] | Temp catergory 1 S3 | 0% | [7 empty] | Temp catergory 1 S3 | 0%
Cl2a S3 | [6 empty] | #N/A | [10 empty] | 1.6 | [31 empty] | Temp catergory 2 S3 |  |  |  | Virus CT Table |  |  |  | Temp | Temp catergory 2 S3 |  |  |  | Virus CT Table |  |  |  | Temp | Temp catergory 2 S3
Cl2b S3 | [6 empty] | #N/A | [10 empty] | 1.8 | [35 empty] | #N/A | #N/A |  | -log | [5 empty] | #N/A | #N/A |  | -log | [8 empty] | Interpolate
|  |  |  | Table # |  |  |  | #N/A |  | #N/A |  | #N/A | [5 empty] | 2 | [18 empty] | V Column Index 1 | [12 empty] | ClOLog C category 1 | 0% |  | #N/A | [5 empty] | O3Log C category 1 | 0% |  | #N/A | [9 empty] | Virus CT Table |  |  |  | Temp
Column Index 1 | [17 empty] | 2.2 | [18 empty] | V Column Index 2 | [12 empty] | ClOLog C category 2 |  |  | #N/A | [5 empty] | O3Log C category 2 |  |  | #N/A | [9 empty] | #N/A | #N/A |  | -log |  | V Column Index 1
Column Index 2 | [17 empty] | 2.4 | [31 empty] | Temp catergory C1 S1 | [8 empty] | Temp catergory C1 S1 | [11 empty] | #N/A | [5 empty] | V Column Index 2
Column Index 3 | [17 empty] | 2.6 | [31 empty] | Temp catergory C2 S1 |  |  |  | Crypto CT Table |  |  |  | Temp | Temp catergory C2 S1 |  |  |  | Crypto CT Table |  |  |  | Temp |  |  |  | #N/A
Column Index 4 | [17 empty] | 2.8 | [31 empty] | Temp cat a |  |  |  | #N/A | #N/A |  | -log |  | Temp cat a |  |  |  | #N/A | #N/A |  | -log
[18 empty] | 3 | [31 empty] | Temp cat b |  |  | #N/A | [5 empty] | Temp cat b |  |  | #N/A
[19 empty] | #N/A |  | #N/A |  | #N/A |  | #N/A |  |  | #N/A |  | #N/A |  |  | pH , | [19 empty] | #N/A | [8 empty] | #N/A
| % Below |  |  | Segment 4 | Giardia CT Cl2 (free) |  |  | Segment 4 |  | CT Values |  | Interpolate pH |  | log-I | Temp | Cl2 |  |  | Segment 4 Required Cl2 for 100% Giardia CT | [8 empty] | Interpolate pH |  |  |  |  | Temperature |  | Log I | [42 empty] | % Below |  | Segment 4 | Microcystin CT Cl2 (free) |  |  |  | Interpolate pH |  | ug/l | Temp |  | Segment 4 Microcystin CT Ozone
Log G category 1 | 0% |  |  | Segment 4 |  |  |  | Segment 4 | [10 empty] | CT Table |  | CT Table |  | CT Table |  | CT Table | [15 empty] | Segment 4 Virus CT Cl2 (free) | [12 empty] | Segment 4 CT Chlorine Dioxide | [8 empty] | Segment 4 CT Ozone | [8 empty] | Segment 4 CT Chloramine |  |  |  |  | Log G category 1 | 0% |  | 0
Log G category 2 | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -log |  | mg/l |  | CL2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | -log |  |  | % Below |  |  | Segment 4 |  |  |  | Interpolate pH |  | log-I |  | Temp |  | % Below |  |  | Segment 4 | [5 empty] | % Below |  |  | Segment 4 | [5 empty] | % Below |  |  | Segment 4 |  |  |  |  | Log G category 2
pH category 1 S4 | 0% | [6 empty] | CT Table |  | CT Table | [7 empty] | 0.4 | [18 empty] | Log V category 1 | 0% | [11 empty] | ClOLog G category 1 | 0% | [5 empty] | Interpolate |  | O3Log G category 1 | 0% | [5 empty] | Interpolate |  | ClALog G category 1 | 0% | [5 empty] | Interpolate |  | pH category 1 S1 | 0% |  |  | Virus CT Table | [9 empty] | CT req.
pH category 2 S4 | [6 empty] | #N/A | [10 empty] | 0.6 | [18 empty] | Log V category 2 |  |  |  | Virus CT Table | [8 empty] | ClOLog G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | O3Log G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | ClALog G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | pH category 2 S1 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ug/l
Temp catergory 1 S4 | 0% | [5 empty] | #N/A | [10 empty] | 0.8 | [18 empty] | pH V category 1 S4 | 0% |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -log |  |  | ClOLog V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | O3Log V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | ClALog V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | Temp catergory 1 S1 | 0% |  | #N/A
Temp catergory 2 S4 | [7 empty] | #N/A |  | #N/A |  | #N/A | [5 empty] | 1 | [18 empty] | pH V category 2 S4 |  |  | #N/A | [9 empty] | ClOLog V category 2 |  |  | #N/A | [5 empty] | O3Log V category 2 |  |  | #N/A | [5 empty] | ClALog V category 2 |  |  | #N/A | [5 empty] | Temp catergory 2 S1 |  |  | #N/A
Cl2 catergory 1 S4 | [17 empty] | 1.2 | [18 empty] | Temp catergory 1 S4 | 0% |  | #N/A | [12 empty] | #N/A | [8 empty] | #N/A | [8 empty] | #N/A | [13 empty] | pH
Cl2 catergory 2 S4 | [7 empty] | CT Table |  | CT Table | [7 empty] | 1.4 | [18 empty] | Temp catergory 2 S4 | [7 empty] | pH |  |  |  |  | Temp catergory 1 S4 | 0% | [7 empty] | Temp catergory 1 S4 | 0% | [7 empty] | Temp catergory 1 S4 | 0%
Cl2a S4 | [6 empty] | #N/A | [10 empty] | 1.6 | [31 empty] | Temp catergory 2 S4 |  |  |  | Virus CT Table |  |  |  | Temp | Temp catergory 2 S4 |  |  |  | Virus CT Table |  |  |  | Temp | Temp catergory 2 S4
Cl2b S4 | [6 empty] | #N/A | [10 empty] | 1.8 | [35 empty] | #N/A | #N/A |  | -log | [5 empty] | #N/A | #N/A |  | -log | [8 empty] | Interpolate
|  |  |  | Table # |  |  |  | #N/A |  | #N/A |  | #N/A | [5 empty] | 2 | [18 empty] | V Column Index 1 | [12 empty] | ClOLog C category 1 | 0% |  | #N/A | [5 empty] | O3Log C category 1 | 0% |  | #N/A | [9 empty] | Virus CT Table |  |  |  | Temp
Column Index 1 | [17 empty] | 2.2 | [18 empty] | V Column Index 2 | [12 empty] | ClOLog C category 2 |  |  | #N/A | [5 empty] | O3Log C category 2 |  |  | #N/A | [9 empty] | #N/A | #N/A |  | -log |  | V Column Index 1
Column Index 2 | [17 empty] | 2.4 | [31 empty] | Temp catergory C1 S1 | [8 empty] | Temp catergory C1 S1 | [11 empty] | #N/A | [5 empty] | V Column Index 2
Column Index 3 | [17 empty] | 2.6 | [31 empty] | Temp catergory C2 S1 |  |  |  | Crypto CT Table |  |  |  | Temp | Temp catergory C2 S1 |  |  |  | Crypto CT Table |  |  |  | Temp |  |  |  | #N/A
Column Index 4 | [17 empty] | 2.8 | [31 empty] | Temp cat a |  |  |  | #N/A | #N/A |  | -log |  | Temp cat a |  |  |  | #N/A | #N/A |  | -log
[18 empty] | 3 | [31 empty] | Temp cat b |  |  | #N/A | [5 empty] | Temp cat b |  |  | #N/A
[19 empty] | #N/A |  | #N/A |  | #N/A |  | #N/A |  |  | #N/A |  | #N/A |  |  | pH , | [19 empty] | #N/A | [8 empty] | #N/A
| % Below |  |  | Segment 5 | Giardia CT Cl2 (free) |  |  | Segment 5 |  | CT Values |  | Interpolate pH |  | log-I | Temp | Cl2 |  |  | Segment 5 Required Cl2 for 100% Giardia CT | [8 empty] | Interpolate pH |  |  |  |  | Temperature |  | Log I | [42 empty] | % Below |  | Segment 5 | Microcystin CT Cl2 (free) |  |  |  | Interpolate pH |  | ug/l | Temp |  | Segment 5 Microcystin CT Ozone
Log G category 1 | 0% |  |  | Pipeline |  |  |  | Pipeline | [10 empty] | CT Table |  | CT Table |  | CT Table |  | CT Table | [15 empty] | Segment 5 Virus CT Cl2 (free) | [12 empty] | Segment 5 CT Chlorine Dioxide | [8 empty] | Segment 5 CT Ozone | [8 empty] | Segment 5 CT Chloramine |  |  |  |  | Log G category 1 | 0% |  | 0
Log G category 2 | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -log |  | mg/l |  | CL2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | -log |  |  | % Below |  |  | Pipeline |  |  |  | Interpolate pH |  | log-I |  | Temp |  | % Below |  |  | Pipeline | [5 empty] | % Below |  |  | Pipeline | [5 empty] | % Below |  |  | Pipeline |  |  |  |  | Log G category 2
pH category 1 S5 | 0% | [6 empty] | CT Table |  | CT Table | [7 empty] | 0.4 | [18 empty] | Log V category 1 | 0% | [11 empty] | ClOLog G category 1 | 0% | [5 empty] | Interpolate |  | O3Log G category 1 | 0% | [5 empty] | Interpolate |  | ClALog G category 1 | 0% | [5 empty] | Interpolate |  | pH category 1 S1 | 0% |  |  | Virus CT Table | [9 empty] | CT req.
pH category 2 S5 | [6 empty] | #N/A | [10 empty] | 0.6 | [18 empty] | Log V category 2 |  |  |  | Virus CT Table | [8 empty] | ClOLog G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | O3Log G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | ClALog G category 2 |  |  |  | Giardia CT Table |  |  |  | Temp | pH category 2 S1 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ug/l
Temp catergory 1 S5 | 0% | [5 empty] | #N/A | [10 empty] | 0.8 | [18 empty] | pH V category 1 S5 | 0% |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | -log |  |  | ClOLog V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | O3Log V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | ClALog V category 1 | 0% |  |  | #N/A | #N/A |  | -log |  | Temp catergory 1 S1 | 0% |  | #N/A
Temp catergory 2 S5 | [7 empty] | #N/A |  | #N/A |  | #N/A | [5 empty] | 1 | [18 empty] | pH V category 2 S5 |  |  | #N/A | [9 empty] | ClOLog V category 2 |  |  | #N/A | [5 empty] | O3Log V category 2 |  |  | #N/A | [5 empty] | ClALog V category 2 |  |  | #N/A | [5 empty] | Temp catergory 2 S1 |  |  | #N/A
Cl2 catergory 1 S5 | [17 empty] | 1.2 | [18 empty] | Temp catergory 1 S5 | 0% |  | #N/A | [12 empty] | #N/A | [8 empty] | #N/A | [8 empty] | #N/A | [13 empty] | pH
Cl2 catergory 2 S5 | [7 empty] | CT Table |  | CT Table | [7 empty] | 1.4 | [18 empty] | Temp catergory 2 S5 | [7 empty] | pH |  |  |  |  | Temp catergory 1 S5 | 0% | [7 empty] | Temp catergory 1 S5 | 0% | [7 empty] | Temp catergory 1 S5 | 0%
Cl2a S5 | [6 empty] | #N/A | [10 empty] | 1.6 | [31 empty] | Temp catergory 2 S5 |  |  |  | Virus CT Table |  |  |  | Temp | Temp catergory 2 S5 |  |  |  | Virus CT Table |  |  |  | Temp | Temp catergory 2 S5
Cl2b S5 | [6 empty] | #N/A | [10 empty] | 1.8 | [35 empty] | #N/A | #N/A |  | -log | [5 empty] | #N/A | #N/A |  | -log | [8 empty] | Interpolate
|  |  |  | Table # |  |  |  | #N/A |  | #N/A |  | #N/A | [5 empty] | 2 | [18 empty] | V Column Index 1 | [12 empty] | ClOLog C category 1 | 0% |  | #N/A | [5 empty] | O3Log C category 1 | 0% |  | #N/A | [9 empty] | Virus CT Table |  |  |  | Temp
Column Index 1 | [17 empty] | 2.2 | [18 empty] | V Column Index 2 | [12 empty] | ClOLog C category 2 |  |  | #N/A | [5 empty] | O3Log C category 2 |  |  | #N/A | [9 empty] | #N/A | #N/A |  | -log |  | V Column Index 1
Column Index 2 | [17 empty] | 2.4 | [31 empty] | Temp catergory C1 S1 | [8 empty] | Temp catergory C1 S1 | [11 empty] | #N/A | [5 empty] | V Column Index 2
Column Index 3 | [17 empty] | 2.6 | [31 empty] | Temp catergory C2 S1 |  |  |  | Crypto CT Table |  |  |  | Temp | Temp catergory C2 S1 |  |  |  | Crypto CT Table |  |  |  | Temp |  |  |  | #N/A
Column Index 4 | [17 empty] | 2.8 | [31 empty] | Temp cat a |  |  |  | #N/A | #N/A |  | -log |  | Temp cat a |  |  |  | #N/A | #N/A |  | -log
[18 empty] | 3 | [31 empty] | Temp cat b |  |  | #N/A | [5 empty] | Temp cat b |  |  | #N/A
[19 empty] | #N/A |  | #N/A |  | #N/A |  | #N/A |  |  | #N/A |  | #N/A |  |  | pH , | [19 empty] | #N/A | [8 empty] | #N/A

## CT Tables (hidden)
Giardia | CL2 | Temperature <= 0.5 C | [41 empty] | Temperature = 5 C | [41 empty] | Temperature = 10 C | [41 empty] | Temperature = 15 C | [41 empty] | Temperature = 20 C | [41 empty] | Temperature = 25 C
CT table | mg/l | pH <=6 Table #1 | [5 empty] | pH =6.5 Table #2 | [5 empty] | pH =7 Table #3 | [5 empty] | pH =7.5 Table #4 | [5 empty] | pH =8 Table #5 | [5 empty] | pH =8.5 Table #6 | [5 empty] | pH =9 Table #7 | [5 empty] | pH <=6 Table #8 | [5 empty] | pH =6.5 Table #9 | [5 empty] | pH =7 Table #10 | [5 empty] | pH =7.5 Table #11 | [5 empty] | pH =8 Table #12 | [5 empty] | pH =8.5 Table #13 | [5 empty] | pH =9 Table #14 | [5 empty] | pH <=6 Table #15 | [5 empty] | pH =6.5 Table #16 | [5 empty] | pH =7 Table #17 | [5 empty] | pH =7.5 Table #18 | [5 empty] | pH =8 Table #19 | [5 empty] | pH =8.5 Table #20 | [5 empty] | pH =9 Table #21 | [5 empty] | pH <=6 Table #22 | [5 empty] | pH =6.5 Table #23 | [5 empty] | pH =7 Table #24 | [5 empty] | pH =7.5 Table #25 | [5 empty] | pH =8 Table #26 | [5 empty] | pH =8.5 Table #27 | [5 empty] | pH =9 Table #28 | [5 empty] | pH <=6 Table #29 | [5 empty] | pH =6.5 Table #30 | [5 empty] | pH =7 Table #31 | [5 empty] | pH =7.5 Table #32 | [5 empty] | pH =8 Table #33 | [5 empty] | pH =8.5 Table #34 | [5 empty] | pH =9 Table #35 | [5 empty] | pH <=6 Table #36 | [5 empty] | pH =6.5 Table #37 | [5 empty] | pH =7 Table #38 | [5 empty] | pH =7.5 Table #39 | [5 empty] | pH =8 Table #40 | [5 empty] | pH =8.5 Table #41 | [5 empty] | pH =9 Table #42
Free Cl2 | logs | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3
Row | Column | 1-1-1 | 1-1-2 | 1-1-3 | 1-1-4 | 1-1-5 | 1-1-6 | 1-2-1 | 1-2-2 | 1-2-3 | 1-2-4 | 1-2-5 | 1-2-6 | 1-3-1 | 1-3-2 | 1-3-3 | 1-3-4 | 1-3-5 | 1-3-6 | 1-4-1 | 1-4-2 | 1-4-3 | 1-4-4 | 1-4-5 | 1-4-6 | 1-5-1 | 1-5-2 | 1-5-3 | 1-5-4 | 1-5-5 | 1-5-6 | 1-6-1 | 1-6-2 | 1-6-3 | 1-6-4 | 1-6-5 | 1-6-6 | 1-7-1 | 1-7-2 | 1-7-3 | 1-7-4 | 1-7-5 | 1-7-6 | 2-1-1 | 2-1-2 | 2-1-3 | 2-1-4 | 2-1-5 | 2-1-6 | 2-2-1 | 2-2-2 | 2-2-3 | 2-2-4 | 2-2-5 | 2-2-6 | 2-3-1 | 2-3-2 | 2-3-3 | 2-3-4 | 2-3-5 | 2-3-6 | 2-4-1 | 2-4-2 | 2-4-3 | 2-4-4 | 2-4-5 | 2-4-6 | 2-5-1 | 2-5-2 | 2-5-3 | 2-5-4 | 2-5-5 | 2-5-6 | 2-6-1 | 2-6-2 | 2-6-3 | 2-6-4 | 2-6-5 | 2-6-6 | 2-7-1 | 2-7-2 | 2-7-3 | 2-7-4 | 2-7-5 | 2-7-6 | 3-1-1 | 3-1-2 | 3-1-3 | 3-1-4 | 3-1-5 | 3-1-6 | 3-2-1 | 3-2-2 | 3-2-3 | 3-2-4 | 3-2-5 | 3-2-6 | 3-3-1 | 3-3-2 | 3-3-3 | 3-3-4 | 3-3-5 | 3-3-6 | 3-4-1 | 3-4-2 | 3-4-3 | 3-4-4 | 3-4-5 | 3-4-6 | 3-5-1 | 3-5-2 | 3-5-3 | 3-5-4 | 3-5-5 | 3-5-6 | 3-6-1 | 3-6-2 | 3-6-3 | 3-6-4 | 3-6-5 | 3-6-6 | 3-7-1 | 3-7-2 | 3-7-3 | 3-7-4 | 3-7-5 | 3-7-6 | 4-1-1 | 4-1-2 | 4-1-3 | 4-1-4 | 4-1-5 | 4-1-6 | 4-2-1 | 4-2-2 | 4-2-3 | 4-2-4 | 4-2-5 | 4-2-6 | 4-3-1 | 4-3-2 | 4-3-3 | 4-3-4 | 4-3-5 | 4-3-6 | 4-4-1 | 4-4-2 | 4-4-3 | 4-4-4 | 4-4-5 | 4-4-6 | 4-5-1 | 4-5-2 | 4-5-3 | 4-5-4 | 4-5-5 | 4-5-6 | 4-6-1 | 4-6-2 | 4-6-3 | 4-6-4 | 4-6-5 | 4-6-6 | 4-7-1 | 4-7-2 | 4-7-3 | 4-7-4 | 4-7-5 | 4-7-6 | 5-1-1 | 5-1-2 | 5-1-3 | 5-1-4 | 5-1-5 | 5-1-6 | 5-2-1 | 5-2-2 | 5-2-3 | 5-2-4 | 5-2-5 | 5-2-6 | 5-3-1 | 5-3-2 | 5-3-3 | 5-3-4 | 5-3-5 | 5-3-6 | 5-4-1 | 5-4-2 | 5-4-3 | 5-4-4 | 5-4-5 | 5-4-6 | 5-5-1 | 5-5-2 | 5-5-3 | 5-5-4 | 5-5-5 | 5-5-6 | 5-6-1 | 5-6-2 | 5-6-3 | 5-6-4 | 5-6-5 | 5-6-6 | 5-7-1 | 5-7-2 | 5-7-3 | 5-7-4 | 5-7-5 | 5-7-6 | 6-1-1 | 6-1-2 | 6-1-3 | 6-1-4 | 6-1-5 | 6-1-6 | 6-2-1 | 6-2-2 | 6-2-3 | 6-2-4 | 6-2-5 | 6-2-6 | 6-3-1 | 6-3-2 | 6-3-3 | 6-3-4 | 6-3-5 | 6-3-6 | 6-4-1 | 6-4-2 | 6-4-3 | 6-4-4 | 6-4-5 | 6-4-6 | 6-5-1 | 6-5-2 | 6-5-3 | 6-5-4 | 6-5-5 | 6-5-6 | 6-6-1 | 6-6-2 | 6-6-3 | 6-6-4 | 6-6-5 | 6-6-6 | 6-7-1 | 6-7-2 | 6-7-3 | 6-7-4 | 6-7-5 | 6-7-6 | 0
1 | 0.4 | 23 | 46 | 69 | 91 | 114 | 137 | 27 | 54 | 82 | 109 | 136 | 163 | 33 | 65 | 98 | 130 | 163 | 195 | 40 | 79 | 119 | 158 | 198 | 237 | 46 | 92 | 139 | 185 | 231 | 277 | 55 | 110 | 165 | 219 | 274 | 329 | 65 | 130 | 195 | 260 | 325 | 390 | 16 | 32 | 49 | 65 | 81 | 97 | 20 | 39 | 59 | 78 | 98 | 117 | 23 | 46 | 70 | 93 | 116 | 139 | 28 | 55 | 83 | 111 | 138 | 166 | 33 | 66 | 99 | 132 | 165 | 198 | 39 | 79 | 118 | 157 | 197 | 236 | 47 | 93 | 104 | 186 | 233 | 279 | 12 | 24 | 37 | 49 | 61 | 73 | 15 | 29 | 44 | 59 | 73 | 88 | 17 | 35 | 52 | 69 | 87 | 104 | 21 | 42 | 63 | 83 | 104 | 125 | 25 | 50 | 75 | 99 | 124 | 149 | 30 | 59 | 89 | 118 | 148 | 177 | 35 | 70 | 105 | 139 | 174 | 209 | 8 | 16 | 25 | 33 | 41 | 49 | 10 | 20 | 30 | 39 | 49 | 59 | 12 | 23 | 35 | 47 | 58 | 70 | 14 | 28 | 42 | 55 | 69 | 83 | 17 | 33 | 50 | 66 | 83 | 99 | 20 | 39 | 59 | 79 | 98 | 118 | 23 | 47 | 70 | 93 | 117 | 140 | 6 | 12 | 18 | 24 | 30 | 36 | 7 | 15 | 22 | 29 | 37 | 44 | 9 | 17 | 26 | 35 | 43 | 52 | 10 | 21 | 31 | 41 | 52 | 62 | 12 | 25 | 37 | 49 | 62 | 74 | 15 | 30 | 45 | 59 | 74 | 89 | 18 | 35 | 53 | 70 | 88 | 105 | 4 | 8 | 12 | 16 | 20 | 24 | 5 | 10 | 15 | 19 | 24 | 29 | 6 | 12 | 18 | 23 | 29 | 35 | 7 | 14 | 21 | 28 | 35 | 42 | 8 | 17 | 25 | 33 | 42 | 50 | 10 | 20 | 30 | 39 | 49 | 59 | 12 | 23 | 35 | 47 | 58 | 70 | 0
2 | 0.6 | 24 | 47 | 71 | 94 | 118 | 141 | 28 | 56 | 84 | 112 | 140 | 168 | 33 | 67 | 100 | 133 | 167 | 200 | 40 | 80 | 120 | 159 | 199 | 239 | 48 | 95 | 143 | 191 | 238 | 286 | 57 | 114 | 171 | 228 | 285 | 342 | 68 | 136 | 204 | 271 | 339 | 407 | 17 | 33 | 50 | 67 | 83 | 100 | 20 | 40 | 60 | 80 | 100 | 120 | 24 | 48 | 72 | 95 | 119 | 143 | 29 | 57 | 86 | 114 | 143 | 171 | 34 | 68 | 102 | 136 | 170 | 204 | 41 | 81 | 122 | 163 | 203 | 244 | 48 | 97 | 146 | 194 | 243 | 291 | 13 | 25 | 38 | 50 | 63 | 75 | 15 | 30 | 45 | 60 | 75 | 90 | 18 | 36 | 54 | 71 | 89 | 107 | 21 | 43 | 64 | 85 | 107 | 128 | 26 | 51 | 77 | 102 | 128 | 153 | 31 | 61 | 92 | 122 | 153 | 183 | 36 | 73 | 109 | 145 | 182 | 218 | 8 | 17 | 25 | 33 | 42 | 50 | 10 | 20 | 30 | 40 | 50 | 60 | 12 | 24 | 36 | 48 | 60 | 72 | 14 | 29 | 43 | 57 | 72 | 86 | 17 | 34 | 51 | 68 | 85 | 102 | 20 | 41 | 61 | 81 | 102 | 122 | 24 | 49 | 73 | 97 | 122 | 146 | 6 | 13 | 19 | 25 | 32 | 38 | 8 | 15 | 23 | 30 | 38 | 45 | 9 | 18 | 27 | 36 | 45 | 54 | 11 | 21 | 32 | 43 | 53 | 64 | 13 | 26 | 39 | 51 | 64 | 77 | 15 | 31 | 46 | 61 | 77 | 92 | 18 | 36 | 55 | 73 | 91 | 109 | 4 | 8 | 13 | 17 | 21 | 25 | 5 | 10 | 15 | 20 | 25 | 30 | 6 | 12 | 18 | 24 | 30 | 36 | 7 | 14 | 22 | 29 | 36 | 43 | 9 | 17 | 26 | 34 | 43 | 51 | 10 | 20 | 31 | 41 | 51 | 61 | 12 | 24 | 37 | 49 | 61 | 73 | 0
3 | 0.8 | 24 | 48 | 70 | 97 | 121 | 145 | 29 | 57 | 86 | 115 | 143 | 172 | 34 | 68 | 103 | 137 | 171 | 205 | 41 | 82 | 123 | 164 | 205 | 246 | 49 | 98 | 148 | 197 | 246 | 295 | 59 | 118 | 177 | 236 | 295 | 354 | 70 | 141 | 211 | 281 | 352 | 422 | 17 | 34 | 52 | 69 | 86 | 103 | 20 | 41 | 61 | 81 | 102 | 122 | 24 | 49 | 73 | 97 | 122 | 146 | 29 | 58 | 88 | 117 | 146 | 175 | 35 | 70 | 105 | 140 | 175 | 210 | 42 | 84 | 126 | 168 | 210 | 252 | 50 | 100 | 151 | 201 | 251 | 301 | 13 | 26 | 39 | 52 | 65 | 78 | 15 | 31 | 46 | 61 | 77 | 92 | 18 | 37 | 55 | 73 | 92 | 110 | 22 | 44 | 66 | 87 | 109 | 131 | 26 | 53 | 79 | 105 | 132 | 158 | 32 | 63 | 95 | 126 | 158 | 189 | 38 | 75 | 113 | 151 | 188 | 226 | 9 | 17 | 26 | 35 | 43 | 52 | 10 | 20 | 31 | 41 | 51 | 61 | 12 | 24 | 37 | 49 | 61 | 73 | 15 | 29 | 44 | 59 | 73 | 88 | 18 | 35 | 53 | 70 | 88 | 105 | 21 | 42 | 63 | 84 | 105 | 126 | 25 | 50 | 76 | 101 | 126 | 151 | 7 | 13 | 20 | 26 | 33 | 39 | 8 | 15 | 23 | 31 | 38 | 46 | 9 | 18 | 28 | 37 | 46 | 55 | 11 | 22 | 33 | 44 | 55 | 66 | 13 | 26 | 40 | 53 | 66 | 79 | 16 | 32 | 48 | 63 | 79 | 95 | 19 | 38 | 57 | 75 | 94 | 113 | 4 | 9 | 13 | 17 | 22 | 26 | 5 | 10 | 16 | 21 | 26 | 31 | 6 | 12 | 19 | 25 | 31 | 37 | 7 | 15 | 22 | 29 | 37 | 44 | 9 | 18 | 27 | 35 | 44 | 53 | 11 | 21 | 32 | 42 | 53 | 63 | 13 | 25 | 38 | 50 | 63 | 75 | 0
4 | 1 | 25 | 49 | 74 | 99 | 123 | 148 | 29 | 59 | 88 | 117 | 147 | 176 | 35 | 70 | 105 | 140 | 175 | 210 | 42 | 84 | 127 | 169 | 211 | 253 | 51 | 101 | 152 | 203 | 253 | 304 | 61 | 122 | 183 | 243 | 304 | 365 | 73 | 146 | 219 | 291 | 364 | 437 | 18 | 35 | 53 | 70 | 88 | 105 | 21 | 42 | 63 | 83 | 104 | 125 | 25 | 50 | 75 | 99 | 124 | 149 | 30 | 60 | 90 | 119 | 149 | 179 | 36 | 72 | 108 | 144 | 180 | 216 | 43 | 87 | 130 | 173 | 217 | 260 | 52 | 104 | 156 | 208 | 260 | 312 | 13 | 26 | 40 | 53 | 66 | 79 | 16 | 31 | 47 | 63 | 78 | 94 | 19 | 37 | 56 | 75 | 93 | 112 | 22 | 45 | 67 | 89 | 112 | 134 | 27 | 54 | 81 | 108 | 135 | 162 | 33 | 65 | 98 | 130 | 163 | 195 | 39 | 78 | 117 | 156 | 195 | 234 | 9 | 18 | 27 | 35 | 44 | 53 | 11 | 21 | 32 | 42 | 53 | 63 | 13 | 25 | 38 | 50 | 63 | 75 | 15 | 30 | 45 | 60 | 75 | 90 | 18 | 36 | 54 | 72 | 90 | 108 | 22 | 43 | 65 | 87 | 108 | 130 | 26 | 52 | 78 | 104 | 130 | 156 | 7 | 13 | 20 | 26 | 33 | 39 | 8 | 16 | 24 | 31 | 39 | 47 | 9 | 19 | 28 | 37 | 47 | 56 | 11 | 22 | 34 | 45 | 56 | 67 | 14 | 27 | 41 | 54 | 68 | 81 | 16 | 33 | 49 | 65 | 82 | 98 | 20 | 39 | 59 | 78 | 98 | 117 | 4 | 9 | 13 | 17 | 22 | 26 | 5 | 10 | 16 | 21 | 26 | 31 | 6 | 12 | 19 | 25 | 31 | 37 | 8 | 15 | 23 | 30 | 38 | 45 | 9 | 18 | 27 | 36 | 45 | 54 | 11 | 22 | 33 | 43 | 54 | 65 | 13 | 26 | 39 | 52 | 65 | 78 | 0
5 | 1.2 | 25 | 51 | 76 | 101 | 127 | 152 | 30 | 60 | 90 | 120 | 150 | 180 | 36 | 72 | 108 | 143 | 179 | 215 | 43 | 86 | 130 | 173 | 216 | 259 | 52 | 104 | 157 | 209 | 261 | 313 | 63 | 125 | 188 | 251 | 313 | 376 | 75 | 150 | 226 | 301 | 376 | 451 | 18 | 36 | 54 | 71 | 89 | 107 | 21 | 42 | 64 | 85 | 106 | 127 | 25 | 51 | 76 | 101 | 127 | 152 | 31 | 61 | 92 | 122 | 153 | 183 | 37 | 74 | 111 | 147 | 184 | 221 | 45 | 89 | 134 | 178 | 223 | 267 | 53 | 107 | 160 | 213 | 267 | 320 | 13 | 27 | 40 | 53 | 67 | 80 | 16 | 32 | 48 | 63 | 79 | 95 | 19 | 38 | 57 | 76 | 95 | 114 | 23 | 46 | 69 | 91 | 114 | 137 | 28 | 55 | 83 | 111 | 138 | 166 | 33 | 67 | 100 | 133 | 167 | 200 | 40 | 80 | 120 | 160 | 200 | 240 | 9 | 18 | 27 | 36 | 45 | 54 | 11 | 21 | 32 | 43 | 53 | 64 | 13 | 25 | 38 | 51 | 63 | 76 | 15 | 31 | 46 | 61 | 77 | 92 | 19 | 37 | 56 | 74 | 93 | 111 | 22 | 45 | 67 | 89 | 112 | 134 | 27 | 53 | 80 | 107 | 133 | 160 | 7 | 13 | 20 | 27 | 33 | 40 | 8 | 16 | 24 | 32 | 40 | 48 | 10 | 19 | 29 | 38 | 48 | 57 | 12 | 23 | 35 | 46 | 58 | 69 | 14 | 28 | 42 | 55 | 69 | 83 | 17 | 33 | 50 | 67 | 83 | 100 | 20 | 40 | 60 | 80 | 100 | 120 | 5 | 9 | 14 | 18 | 23 | 27 | 5 | 11 | 16 | 21 | 27 | 32 | 6 | 13 | 19 | 25 | 32 | 38 | 8 | 15 | 23 | 31 | 38 | 46 | 9 | 18 | 28 | 37 | 46 | 55 | 11 | 22 | 34 | 45 | 56 | 67 | 13 | 27 | 40 | 53 | 67 | 80 | 0
6 | 1.4 | 26 | 52 | 78 | 103 | 129 | 155 | 31 | 61 | 92 | 123 | 153 | 184 | 37 | 74 | 111 | 147 | 184 | 221 | 44 | 89 | 133 | 177 | 222 | 266 | 54 | 107 | 161 | 214 | 268 | 321 | 65 | 129 | 194 | 258 | 323 | 387 | 77 | 155 | 232 | 309 | 387 | 464 | 18 | 36 | 55 | 73 | 91 | 109 | 22 | 43 | 65 | 87 | 108 | 130 | 26 | 52 | 78 | 103 | 129 | 155 | 31 | 62 | 94 | 125 | 156 | 187 | 38 | 76 | 114 | 151 | 489 | 227 | 46 | 91 | 137 | 183 | 228 | 274 | 55 | 110 | 165 | 219 | 274 | 329 | 14 | 27 | 41 | 55 | 68 | 82 | 16 | 33 | 49 | 65 | 82 | 98 | 19 | 39 | 58 | 77 | 97 | 116 | 23 | 47 | 70 | 93 | 117 | 140 | 28 | 57 | 85 | 113 | 142 | 170 | 34 | 69 | 103 | 137 | 172 | 206 | 41 | 82 | 124 | 165 | 206 | 247 | 9 | 18 | 28 | 37 | 46 | 55 | 11 | 22 | 33 | 43 | 54 | 65 | 13 | 26 | 39 | 52 | 65 | 78 | 16 | 31 | 47 | 63 | 78 | 94 | 19 | 38 | 57 | 76 | 95 | 114 | 23 | 46 | 69 | 91 | 114 | 137 | 28 | 55 | 83 | 110 | 138 | 165 | 7 | 14 | 21 | 27 | 34 | 41 | 8 | 16 | 25 | 33 | 41 | 49 | 10 | 19 | 29 | 39 | 48 | 58 | 12 | 23 | 35 | 47 | 58 | 70 | 14 | 28 | 43 | 57 | 71 | 85 | 17 | 34 | 52 | 69 | 86 | 103 | 21 | 41 | 62 | 82 | 103 | 123 | 5 | 9 | 14 | 18 | 23 | 27 | 6 | 11 | 17 | 22 | 28 | 33 | 7 | 13 | 20 | 26 | 33 | 39 | 8 | 16 | 24 | 31 | 39 | 47 | 10 | 19 | 29 | 38 | 48 | 57 | 12 | 23 | 35 | 46 | 58 | 69 | 14 | 27 | 41 | 55 | 68 | 82 | 0
7 | 1.6 | 26 | 52 | 79 | 105 | 131 | 157 | 32 | 63 | 95 | 126 | 158 | 189 | 38 | 75 | 113 | 151 | 188 | 226 | 46 | 91 | 137 | 182 | 228 | 273 | 55 | 110 | 165 | 219 | 274 | 329 | 66 | 132 | 199 | 265 | 331 | 397 | 80 | 159 | 239 | 318 | 398 | 477 | 19 | 37 | 56 | 74 | 93 | 111 | 22 | 44 | 66 | 88 | 110 | 132 | 26 | 53 | 79 | 105 | 132 | 158 | 32 | 64 | 96 | 128 | 160 | 192 | 39 | 77 | 116 | 155 | 193 | 232 | 47 | 94 | 141 | 187 | 234 | 281 | 56 | 112 | 169 | 225 | 281 | 337 | 14 | 28 | 42 | 55 | 69 | 83 | 17 | 33 | 50 | 66 | 83 | 99 | 20 | 40 | 60 | 79 | 99 | 119 | 24 | 48 | 72 | 96 | 120 | 144 | 29 | 58 | 87 | 116 | 145 | 174 | 35 | 70 | 106 | 141 | 176 | 211 | 42 | 84 | 127 | 169 | 211 | 253 | 9 | 19 | 28 | 37 | 47 | 56 | 11 | 22 | 33 | 44 | 55 | 66 | 13 | 26 | 40 | 53 | 66 | 79 | 16 | 32 | 48 | 64 | 80 | 96 | 19 | 39 | 58 | 77 | 97 | 116 | 24 | 47 | 71 | 94 | 118 | 141 | 28 | 56 | 85 | 113 | 141 | 169 | 7 | 14 | 21 | 28 | 35 | 42 | 8 | 17 | 25 | 33 | 42 | 50 | 10 | 20 | 30 | 39 | 49 | 59 | 12 | 24 | 36 | 48 | 60 | 72 | 15 | 29 | 44 | 58 | 73 | 87 | 18 | 35 | 53 | 70 | 88 | 105 | 21 | 42 | 63 | 84 | 105 | 126 | 5 | 9 | 14 | 19 | 23 | 28 | 6 | 11 | 17 | 22 | 28 | 33 | 7 | 13 | 20 | 27 | 33 | 40 | 8 | 16 | 24 | 32 | 40 | 48 | 10 | 19 | 29 | 39 | 48 | 58 | 12 | 23 | 35 | 47 | 58 | 70 | 14 | 28 | 42 | 56 | 70 | 84 | 0
8 | 1.8 | 27 | 54 | 81 | 108 | 135 | 162 | 32 | 64 | 97 | 129 | 161 | 193 | 39 | 77 | 116 | 154 | 193 | 231 | 47 | 93 | 140 | 186 | 233 | 279 | 56 | 113 | 169 | 225 | 282 | 338 | 68 | 136 | 204 | 271 | 339 | 407 | 82 | 163 | 245 | 326 | 408 | 489 | 19 | 38 | 57 | 76 | 95 | 114 | 23 | 45 | 68 | 90 | 113 | 135 | 27 | 54 | 81 | 108 | 135 | 162 | 33 | 65 | 98 | 131 | 163 | 196 | 40 | 79 | 119 | 159 | 198 | 238 | 48 | 96 | 144 | 191 | 239 | 287 | 58 | 115 | 173 | 230 | 288 | 345 | 14 | 29 | 43 | 57 | 72 | 86 | 17 | 34 | 51 | 67 | 84 | 101 | 20 | 41 | 61 | 81 | 102 | 122 | 25 | 49 | 74 | 98 | 123 | 147 | 30 | 60 | 90 | 119 | 149 | 179 | 36 | 72 | 108 | 143 | 179 | 215 | 43 | 86 | 130 | 173 | 216 | 259 | 10 | 19 | 29 | 38 | 48 | 57 | 11 | 23 | 34 | 45 | 57 | 68 | 14 | 27 | 41 | 54 | 68 | 81 | 16 | 33 | 49 | 65 | 82 | 98 | 20 | 40 | 60 | 79 | 99 | 119 | 24 | 48 | 72 | 96 | 120 | 144 | 29 | 58 | 87 | 115 | 144 | 173 | 7 | 14 | 22 | 29 | 36 | 43 | 9 | 17 | 26 | 34 | 43 | 51 | 10 | 20 | 31 | 41 | 51 | 61 | 12 | 25 | 37 | 49 | 62 | 74 | 15 | 30 | 45 | 59 | 74 | 89 | 18 | 36 | 54 | 72 | 90 | 108 | 22 | 43 | 65 | 86 | 108 | 129 | 5 | 10 | 15 | 19 | 24 | 29 | 6 | 11 | 17 | 23 | 28 | 34 | 7 | 14 | 21 | 27 | 34 | 41 | 8 | 16 | 25 | 33 | 41 | 49 | 10 | 20 | 30 | 40 | 50 | 60 | 12 | 24 | 36 | 48 | 60 | 72 | 14 | 29 | 43 | 57 | 72 | 86 | 0
9 | 2 | 28 | 55 | 83 | 110 | 138 | 165 | 33 | 66 | 99 | 131 | 164 | 197 | 39 | 79 | 118 | 157 | 197 | 236 | 48 | 95 | 143 | 191 | 238 | 286 | 58 | 115 | 173 | 231 | 288 | 346 | 70 | 139 | 209 | 278 | 348 | 417 | 83 | 167 | 250 | 333 | 417 | 500 | 19 | 39 | 58 | 77 | 97 | 116 | 23 | 46 | 69 | 92 | 115 | 138 | 28 | 55 | 83 | 110 | 138 | 165 | 33 | 67 | 100 | 133 | 167 | 200 | 41 | 81 | 122 | 162 | 203 | 243 | 49 | 98 | 147 | 196 | 245 | 294 | 59 | 118 | 177 | 235 | 294 | 353 | 15 | 29 | 44 | 58 | 73 | 87 | 17 | 35 | 52 | 69 | 87 | 104 | 21 | 41 | 62 | 83 | 103 | 124 | 25 | 50 | 75 | 100 | 125 | 150 | 30 | 61 | 91 | 121 | 152 | 182 | 37 | 74 | 111 | 147 | 184 | 221 | 44 | 88 | 133 | 177 | 221 | 265 | 10 | 19 | 29 | 39 | 48 | 58 | 12 | 23 | 35 | 46 | 58 | 69 | 14 | 28 | 42 | 55 | 69 | 83 | 17 | 33 | 50 | 67 | 83 | 100 | 20 | 41 | 61 | 81 | 102 | 122 | 25 | 49 | 74 | 98 | 123 | 147 | 30 | 59 | 89 | 118 | 148 | 177 | 7 | 15 | 22 | 29 | 37 | 44 | 9 | 17 | 26 | 35 | 43 | 52 | 10 | 21 | 31 | 41 | 52 | 62 | 13 | 25 | 38 | 50 | 63 | 75 | 15 | 30 | 46 | 61 | 76 | 91 | 18 | 37 | 55 | 73 | 92 | 110 | 22 | 44 | 66 | 88 | 110 | 132 | 5 | 10 | 15 | 19 | 24 | 29 | 6 | 12 | 18 | 23 | 29 | 35 | 7 | 14 | 21 | 27 | 35 | 41 | 8 | 17 | 25 | 33 | 42 | 50 | 10 | 20 | 31 | 41 | 51 | 61 | 12 | 25 | 37 | 49 | 62 | 74 | 15 | 29 | 44 | 59 | 73 | 88 | 0
10 | 2.2 | 28 | 56 | 85 | 113 | 141 | 169 | 34 | 67 | 101 | 134 | 168 | 201 | 40 | 81 | 121 | 161 | 202 | 242 | 50 | 99 | 149 | 198 | 248 | 297 | 59 | 118 | 177 | 235 | 294 | 353 | 71 | 142 | 213 | 284 | 355 | 426 | 85 | 170 | 256 | 341 | 426 | 511 | 20 | 39 | 59 | 79 | 98 | 118 | 23 | 47 | 70 | 93 | 117 | 140 | 28 | 56 | 85 | 113 | 141 | 169 | 34 | 68 | 102 | 136 | 170 | 204 | 41 | 83 | 124 | 165 | 207 | 248 | 50 | 100 | 150 | 200 | 250 | 300 | 60 | 120 | 181 | 241 | 301 | 361 | 15 | 30 | 45 | 59 | 74 | 89 | 18 | 35 | 53 | 70 | 88 | 105 | 21 | 42 | 64 | 85 | 106 | 127 | 26 | 51 | 77 | 102 | 128 | 153 | 31 | 62 | 93 | 124 | 155 | 186 | 38 | 75 | 113 | 150 | 188 | 225 | 45 | 90 | 136 | 181 | 226 | 271 | 10 | 20 | 30 | 39 | 49 | 59 | 12 | 23 | 35 | 47 | 58 | 70 | 14 | 28 | 43 | 57 | 71 | 85 | 17 | 34 | 51 | 68 | 85 | 102 | 21 | 41 | 62 | 83 | 103 | 124 | 25 | 50 | 75 | 100 | 125 | 150 | 30 | 60 | 91 | 121 | 151 | 181 | 7 | 15 | 22 | 29 | 37 | 44 | 9 | 18 | 27 | 35 | 44 | 53 | 11 | 21 | 32 | 42 | 53 | 63 | 13 | 26 | 39 | 51 | 64 | 77 | 16 | 31 | 47 | 62 | 78 | 93 | 19 | 38 | 57 | 75 | 94 | 113 | 23 | 45 | 68 | 90 | 113 | 135 | 5 | 10 | 15 | 20 | 25 | 30 | 6 | 12 | 18 | 23 | 29 | 35 | 7 | 14 | 21 | 28 | 36 | 42 | 9 | 17 | 26 | 34 | 43 | 51 | 10 | 21 | 31 | 41 | 52 | 62 | 13 | 25 | 38 | 50 | 63 | 75 | 15 | 30 | 45 | 60 | 75 | 90 | 0
11 | 2.4 | 29 | 57 | 86 | 115 | 143 | 172 | 34 | 68 | 103 | 137 | 171 | 205 | 41 | 82 | 124 | 165 | 206 | 247 | 50 | 99 | 149 | 199 | 248 | 298 | 60 | 120 | 181 | 241 | 301 | 361 | 73 | 145 | 218 | 290 | 363 | 435 | 87 | 174 | 261 | 348 | 435 | 522 | 20 | 40 | 60 | 80 | 100 | 120 | 24 | 48 | 72 | 95 | 119 | 143 | 29 | 57 | 86 | 115 | 143 | 172 | 35 | 70 | 105 | 139 | 174 | 209 | 42 | 84 | 127 | 169 | 211 | 253 | 51 | 102 | 153 | 204 | 255 | 306 | 61 | 123 | 184 | 245 | 307 | 368 | 15 | 30 | 45 | 60 | 75 | 90 | 18 | 36 | 54 | 71 | 89 | 107 | 22 | 43 | 65 | 86 | 108 | 129 | 26 | 52 | 79 | 105 | 131 | 157 | 32 | 63 | 95 | 127 | 158 | 190 | 38 | 77 | 115 | 153 | 192 | 230 | 46 | 92 | 138 | 184 | 230 | 276 | 10 | 20 | 30 | 40 | 50 | 60 | 12 | 24 | 36 | 48 | 60 | 72 | 14 | 29 | 43 | 57 | 72 | 86 | 18 | 35 | 53 | 70 | 88 | 105 | 21 | 42 | 64 | 85 | 106 | 127 | 26 | 51 | 77 | 102 | 128 | 153 | 31 | 61 | 92 | 123 | 153 | 184 | 8 | 15 | 23 | 30 | 38 | 45 | 9 | 18 | 27 | 36 | 45 | 54 | 11 | 22 | 33 | 43 | 54 | 65 | 13 | 26 | 39 | 52 | 65 | 78 | 16 | 32 | 48 | 63 | 79 | 95 | 19 | 38 | 58 | 77 | 96 | 115 | 23 | 46 | 69 | 92 | 115 | 138 | 5 | 10 | 15 | 20 | 25 | 30 | 6 | 12 | 18 | 24 | 30 | 36 | 7 | 14 | 22 | 29 | 37 | 43 | 9 | 17 | 26 | 35 | 43 | 52 | 11 | 21 | 32 | 42 | 53 | 63 | 13 | 26 | 39 | 51 | 64 | 77 | 15 | 31 | 46 | 61 | 77 | 92 | 0
12 | 2.6 | 29 | 58 | 88 | 117 | 146 | 175 | 35 | 70 | 105 | 139 | 174 | 209 | 42 | 84 | 126 | 168 | 210 | 252 | 51 | 101 | 152 | 203 | 253 | 304 | 61 | 123 | 184 | 245 | 307 | 368 | 74 | 148 | 222 | 296 | 370 | 444 | 89 | 178 | 267 | 355 | 444 | 533 | 20 | 41 | 61 | 81 | 102 | 122 | 24 | 49 | 73 | 97 | 122 | 146 | 29 | 58 | 88 | 117 | 146 | 175 | 36 | 71 | 107 | 142 | 178 | 213 | 43 | 86 | 129 | 172 | 215 | 258 | 52 | 104 | 156 | 208 | 260 | 312 | 63 | 125 | 188 | 250 | 313 | 375 | 15 | 31 | 46 | 61 | 77 | 92 | 18 | 37 | 55 | 73 | 92 | 110 | 22 | 44 | 66 | 87 | 109 | 131 | 27 | 53 | 80 | 107 | 133 | 160 | 32 | 65 | 97 | 129 | 162 | 194 | 39 | 78 | 117 | 156 | 195 | 234 | 47 | 94 | 141 | 187 | 234 | 281 | 10 | 20 | 31 | 41 | 51 | 61 | 12 | 24 | 37 | 49 | 61 | 73 | 15 | 29 | 44 | 59 | 73 | 88 | 18 | 36 | 54 | 71 | 89 | 107 | 22 | 43 | 65 | 86 | 108 | 129 | 26 | 52 | 78 | 104 | 130 | 156 | 31 | 63 | 94 | 125 | 157 | 188 | 8 | 15 | 23 | 31 | 38 | 46 | 9 | 18 | 28 | 37 | 46 | 55 | 11 | 22 | 33 | 44 | 55 | 66 | 13 | 27 | 40 | 53 | 67 | 80 | 16 | 32 | 49 | 65 | 81 | 97 | 20 | 39 | 59 | 78 | 98 | 117 | 24 | 47 | 71 | 94 | 118 | 141 | 5 | 10 | 16 | 21 | 26 | 31 | 6 | 12 | 19 | 25 | 31 | 37 | 7 | 15 | 22 | 29 | 37 | 44 | 9 | 18 | 27 | 35 | 44 | 53 | 11 | 22 | 33 | 43 | 54 | 65 | 13 | 26 | 39 | 52 | 65 | 78 | 16 | 31 | 47 | 63 | 78 | 94 | 0
13 | 2.8 | 30 | 59 | 89 | 119 | 148 | 178 | 36 | 71 | 107 | 142 | 178 | 213 | 43 | 86 | 129 | 171 | 214 | 257 | 52 | 103 | 155 | 207 | 258 | 310 | 63 | 125 | 188 | 250 | 313 | 375 | 75 | 151 | 226 | 301 | 377 | 452 | 91 | 181 | 272 | 362 | 453 | 543 | 21 | 41 | 62 | 83 | 103 | 124 | 25 | 49 | 74 | 99 | 123 | 148 | 30 | 59 | 89 | 119 | 148 | 178 | 36 | 72 | 109 | 145 | 181 | 217 | 44 | 88 | 132 | 175 | 219 | 263 | 53 | 106 | 159 | 212 | 265 | 318 | 64 | 127 | 191 | 255 | 318 | 382 | 16 | 31 | 47 | 62 | 78 | 93 | 19 | 37 | 56 | 74 | 93 | 111 | 22 | 45 | 67 | 89 | 112 | 134 | 27 | 54 | 82 | 109 | 136 | 163 | 33 | 66 | 99 | 131 | 164 | 197 | 40 | 80 | 120 | 159 | 199 | 239 | 48 | 96 | 144 | 191 | 239 | 287 | 10 | 21 | 31 | 41 | 52 | 62 | 12 | 25 | 37 | 49 | 62 | 74 | 15 | 30 | 45 | 59 | 74 | 89 | 18 | 36 | 55 | 73 | 91 | 109 | 22 | 44 | 66 | 88 | 110 | 132 | 27 | 53 | 80 | 106 | 133 | 159 | 32 | 64 | 96 | 127 | 159 | 191 | 8 | 16 | 24 | 31 | 39 | 47 | 9 | 19 | 28 | 37 | 47 | 56 | 11 | 22 | 34 | 45 | 56 | 67 | 14 | 27 | 41 | 54 | 68 | 81 | 17 | 33 | 50 | 66 | 83 | 99 | 20 | 40 | 60 | 79 | 99 | 119 | 24 | 48 | 72 | 95 | 119 | 143 | 5 | 10 | 16 | 21 | 26 | 31 | 6 | 12 | 19 | 25 | 31 | 37 | 8 | 15 | 23 | 30 | 38 | 45 | 9 | 18 | 27 | 36 | 45 | 54 | 11 | 22 | 33 | 44 | 55 | 66 | 13 | 27 | 40 | 53 | 67 | 80 | 16 | 32 | 48 | 64 | 80 | 96 | 0
14 | 3 | 30 | 60 | 91 | 121 | 151 | 181 | 36 | 72 | 109 | 145 | 181 | 217 | 44 | 87 | 131 | 174 | 218 | 261 | 53 | 105 | 158 | 211 | 263 | 316 | 64 | 127 | 191 | 255 | 318 | 382 | 77 | 153 | 230 | 307 | 383 | 460 | 92 | 184 | 276 | 368 | 460 | 552 | 21 | 42 | 63 | 84 | 105 | 126 | 25 | 50 | 76 | 101 | 126 | 151 | 30 | 61 | 91 | 121 | 152 | 182 | 37 | 74 | 111 | 147 | 184 | 221 | 45 | 89 | 134 | 179 | 223 | 268 | 54 | 108 | 162 | 216 | 270 | 324 | 65 | 130 | 195 | 259 | 324 | 389 | 16 | 32 | 48 | 63 | 79 | 95 | 19 | 38 | 57 | 75 | 94 | 113 | 23 | 46 | 69 | 91 | 114 | 137 | 28 | 55 | 83 | 111 | 138 | 166 | 34 | 67 | 101 | 134 | 168 | 201 | 41 | 81 | 122 | 162 | 203 | 243 | 49 | 97 | 146 | 195 | 243 | 292 | 11 | 21 | 32 | 42 | 53 | 63 | 13 | 25 | 38 | 51 | 63 | 76 | 15 | 30 | 46 | 61 | 76 | 91 | 19 | 37 | 56 | 74 | 93 | 111 | 22 | 45 | 67 | 89 | 112 | 134 | 27 | 54 | 81 | 108 | 135 | 162 | 33 | 65 | 98 | 130 | 163 | 195 | 8 | 16 | 24 | 31 | 39 | 47 | 10 | 19 | 29 | 38 | 48 | 57 | 11 | 23 | 34 | 45 | 57 | 68 | 14 | 28 | 42 | 55 | 69 | 83 | 17 | 33 | 51 | 67 | 84 | 101 | 20 | 41 | 61 | 81 | 102 | 122 | 24 | 49 | 73 | 97 | 122 | 146 | 5 | 11 | 16 | 21 | 27 | 32 | 6 | 13 | 19 | 25 | 32 | 38 | 8 | 15 | 23 | 31 | 38 | 46 | 9 | 18 | 28 | 37 | 46 | 55 | 11 | 22 | 34 | 45 | 56 | 67 | 14 | 27 | 41 | 54 | 68 | 81 | 16 | 32 | 49 | 65 | 81 | 97 | 0
| pH | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9
| Temp | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
| Table | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 29 | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 39 | 39 | 39 | 39 | 39 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 42 | 42
Category | Inactvation
1 | .5-log
2 | 1-log
3 | 1.5-log
4 | 2-log
5 | 2.5-log
6 | 3-log
0 | 0-log
Virus CT Table for Free Cl2
Virus log Category |  | 1-1 | 1-2 | 1-3 | 2-1 | 2-2 | 2-3 | 0
| Temp C | 2-log | 3-log | 4-log | 2-log | 3-log | 4-log | 0-log
1 | 0.5 | 6 | 9 | 12 | 45 | 66 | 90 | 0
2 | 5 | 4 | 6 | 8 | 30 | 44 | 60 | 0
3 | 10 | 3 | 4 | 6 | 22 | 33 | 45 | 0
4 | 15 | 2 | 3 | 4 | 15 | 22 | 30 | 0
5 | 20 | 1 | 2 | 3 | 11 | 16 | 22 | 0
6 | 25 | 1 | 1 | 2 | 7 | 11 | 15 | 0
|  | pH 6-9 |  |  | pH 10
Giardia CT Table for Chlorine Dioxide
Giardia log Category |  | 1 | 2 | 3 | 4 | 5 | 6 | 0
| Temp C | 0.5-log | 1-log | 1.5-log | 2-log | 2.5-log | 3-log | 0-log
1 | 1 | 10 | 21 | 32 | 42 | 52 | 63 | 0
2 | 5 | 4.3 | 8.7 | 13 | 17 | 22 | 26 | 0
3 | 10 | 4 | 7.7 | 12 | 15 | 19 | 23 | 0
4 | 15 | 3.2 | 6.3 | 10 | 13 | 16 | 19 | 0
5 | 20 | 2.5 | 5 | 7.5 | 10 | 13 | 15 | 0
6 | 25 | 2 | 3.7 | 5.5 | 7.3 | 9 | 11 | 0
Virus CT Table for Chlorine Dioxide
Virus log Category |  | Giardia CT Table for Chlorine Dioxide 1: 1; Giardia CT Table for Chlorine Dioxide 2: 2; Giardia CT Table for Chlorine Dioxide 3: 3; Giardia CT Table for Chlorine Dioxide 4: 0
| Temp C | Giardia CT Table for Chlorine Dioxide 1: 2-log; Giardia CT Table for Chlorine Dioxide 2: 3-log; Giardia CT Table for Chlorine Dioxide 3: 4-log; Giardia CT Table for Chlorine Dioxide 4: 0-log
1 | 1 | 8.4 | 25.6 | 50.1 | 0 |  | pH 6-9
2 | 5 | Giardia CT Table for Chlorine Dioxide 1: 5.6; Giardia CT Table for Chlorine Dioxide 2: 17.1; Giardia CT Table for Chlorine Dioxide 3: 33.4; Giardia CT Table for Chlorine Dioxide 4: 0
3 | 10 | Giardia CT Table for Chlorine Dioxide 1: 4.2; Giardia CT Table for Chlorine Dioxide 2: 12.8; Giardia CT Table for Chlorine Dioxide 3: 25.1; Giardia CT Table for Chlorine Dioxide 4: 0
4 | 15 | Giardia CT Table for Chlorine Dioxide 1: 2.8; Giardia CT Table for Chlorine Dioxide 2: 8.6; Giardia CT Table for Chlorine Dioxide 3: 16.7; Giardia CT Table for Chlorine Dioxide 4: 0
5 | 20 | Giardia CT Table for Chlorine Dioxide 1: 2.1; Giardia CT Table for Chlorine Dioxide 2: 6.4; Giardia CT Table for Chlorine Dioxide 3: 12.5; Giardia CT Table for Chlorine Dioxide 4: 0
6 | 25 | Giardia CT Table for Chlorine Dioxide 1: 1.4; Giardia CT Table for Chlorine Dioxide 2: 4.3; Giardia CT Table for Chlorine Dioxide 3: 8.4; Giardia CT Table for Chlorine Dioxide 4: 0
Crypto CT Table for Chlorine Dioxide
Crypto log Category |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 0
| Temp C | 0.25-log | 0.5-log | 1-log | 1.5-log | 2-log | 2.5-log | 3-log | 0-log
1 | 0.5 | 159 | 319 | 637 | 956 | 1275 | 1594 | 1912 | 0
2 | 1 | 153 | 305 | 610 | 915 | 1220 | 1525 | 1830 | 0
3 | 2 | 140 | 279 | 558 | 838 | 1117 | 1396 | 1675 | 0
4 | 3 | 128 | 256 | 511 | 767 | 1023 | 1278 | 1534 | 0
5 | 5 | 107 | 214 | 429 | 643 | 858 | 1072 | 1286 | 0
6 | 7 | 90 | 180 | 360 | 539 | 719 | 899 | 1079 | 0
7 | 10 | 69 | 138 | 277 | 415 | 553 | 691 | 830 | 0
8 | 15 | 45 | 89 | 179 | 268 | 357 | 447 | 536 | 0
9 | 20 | 29 | 58 | 116 | 174 | 232 | 289 | 347 | 0
10 | 25 | 19 | 38 | 75 | 113 | 150 | 188 | 226 | 0
11 | 30 | 12 | 24 | 49 | 73 | 98 | 122 | 147 | 0
Giardia CT Table for Ozone
Giardia log Category |  | 1 | 2 | 3 | 4 | 5 | 6 | 0
| Temp C | 0.5-log | 1-log | 1.5-log | 2-log | 2.5-log | 3-log | 0-log
1 | 1 | 0.48 | 0.97 | 1.5 | 1.9 | 2.4 | 2.9 | 0
2 | 5 | 0.32 | 0.63 | 0.95 | 1.3 | 1.6 | 1.9 | 0
3 | 10 | 0.23 | 0.48 | 0.72 | 0.95 | 1.2 | 1.43 | 0
4 | 15 | 0.16 | 0.32 | 0.48 | 0.63 | 0.79 | 0.95 | 0
5 | 20 | 0.12 | 0.24 | 0.36 | 0.48 | 0.6 | 0.72 | 0
6 | 25 | 0.08 | 0.16 | 0.24 | 0.32 | 0.4 | 0.48 | 0
Virus CT Table for Ozone
Virus log Category |  | Giardia CT Table for Ozone 1: 1; Giardia CT Table for Ozone 2: 2; Giardia CT Table for Ozone 3: 3; Giardia CT Table for Ozone 4: 0
| Temp C | Giardia CT Table for Ozone 1: 2-log; Giardia CT Table for Ozone 2: 3-log; Giardia CT Table for Ozone 3: 4-log; Giardia CT Table for Ozone 4: 0-log
1 | 1 | Giardia CT Table for Ozone 1: 0.9; Giardia CT Table for Ozone 2: 1.4; Giardia CT Table for Ozone 3: 1.8; Giardia CT Table for Ozone 4: 0
2 | 5 | Giardia CT Table for Ozone 1: 0.6; Giardia CT Table for Ozone 2: 0.9; Giardia CT Table for Ozone 3: 1.2; Giardia CT Table for Ozone 4: 0
3 | 10 | Giardia CT Table for Ozone 1: 0.5; Giardia CT Table for Ozone 2: 0.8; Giardia CT Table for Ozone 3: 1; Giardia CT Table for Ozone 4: 0
4 | 15 | Giardia CT Table for Ozone 1: 0.3; Giardia CT Table for Ozone 2: 0.5; Giardia CT Table for Ozone 3: 0.6; Giardia CT Table for Ozone 4: 0
5 | 20 | Giardia CT Table for Ozone 1: 0.25; Giardia CT Table for Ozone 2: 0.4; Giardia CT Table for Ozone 3: 0.5; Giardia CT Table for Ozone 4: 0
6 | 25 | Giardia CT Table for Ozone 1: 0.15; Giardia CT Table for Ozone 2: 0.25; Giardia CT Table for Ozone 3: 0.3; Giardia CT Table for Ozone 4: 0
Crypto CT Table for Ozone
Crypto log Category |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 0
| Temp C | 0.25-log | 0.5-log | 1-log | 1.5-log | 2-log | 2.5-log | 3-log | 0-log
1 | 0.5 | 6 | 12 | 24 | 36 | 48 | 60 | 72 | 0
2 | 1 | 5.8 | 12 | 23 | 35 | 46 | 58 | 69 | 0
3 | 2 | 5.2 | 10 | 21 | 31 | 42 | 52 | 63 | 0
4 | 3 | 4.8 | 9.5 | 19 | 29 | 38 | 48 | 57 | 0
5 | 5 | 4 | 7.9 | 16 | 24 | 32 | 40 | 47 | 0
6 | 7 | 3.3 | 6.5 | 13 | 20 | 26 | 33 | 39 | 0
7 | 10 | 2.5 | 4.9 | 9.9 | 15 | 20 | 25 | 30 | 0
8 | 15 | 1.6 | 3.1 | 6.2 | 9.3 | 12 | 16 | 19 | 0
9 | 20 | 1 | 2 | 3.9 | 5.9 | 7.8 | 9.8 | 12 | 0
10 | 25 | 0.6 | 1.2 | 2.5 | 3.7 | 4.9 | 6.2 | 7.4 | 0
11 | 30 | 0.39 | 0.78 | 1.6 | 2.4 | 3.1 | 3.9 | 4.7 | 0
Giardia CT Table for Chloramine
Giardia log Category |  | 1 | 2 | 3 | 4 | 5 | 6 | 0
| Temp C | 0.5-log | 1-log | 1.5-log | 2-log | 2.5-log | 3-log | 0-log
1 | 1 | 635 | 1270 | 1900 | 2535 | 3170 | 3800 | 0
2 | 5 | 365 | 735 | 1100 | 1470 | 1830 | 2200 | 0
3 | 10 | 310 | 615 | 930 | 1230 | 1540 | 1850 | 0
4 | 15 | 250 | 500 | 750 | 1000 | 1250 | 1500 | 0
5 | 20 | 185 | 370 | 550 | 735 | 915 | 1100 | 0
6 | 25 | 125 | 250 | 375 | 500 | 625 | 750 | 0
pH 6-9
Virus CT Table for Chloramine
Virus log Category |  | Giardia CT Table for Chloramine 1: 1; Giardia CT Table for Chloramine 2: 2; Giardia CT Table for Chloramine 3: 3; Giardia CT Table for Chloramine 4: 0
| Temp C | Giardia CT Table for Chloramine 1: 2-log; Giardia CT Table for Chloramine 2: 3-log; Giardia CT Table for Chloramine 3: 4-log; Giardia CT Table for Chloramine 4: 0-log
1 | 1 | Giardia CT Table for Chloramine 1: 1243; Giardia CT Table for Chloramine 2: 2063; Giardia CT Table for Chloramine 3: 2883; Giardia CT Table for Chloramine 4: 0
2 | 5 | Giardia CT Table for Chloramine 1: 857; Giardia CT Table for Chloramine 2: 1423; Giardia CT Table for Chloramine 3: 1988; Giardia CT Table for Chloramine 4: 0
3 | 10 | Giardia CT Table for Chloramine 1: 643; Giardia CT Table for Chloramine 2: 1067; Giardia CT Table for Chloramine 3: 1491; Giardia CT Table for Chloramine 4: 0
4 | 15 | Giardia CT Table for Chloramine 1: 428; Giardia CT Table for Chloramine 2: 712; Giardia CT Table for Chloramine 3: 994; Giardia CT Table for Chloramine 4: 0
5 | 20 | Giardia CT Table for Chloramine 1: 321; Giardia CT Table for Chloramine 2: 534; Giardia CT Table for Chloramine 3: 746; Giardia CT Table for Chloramine 4: 0
6 | 25 | Giardia CT Table for Chloramine 1: 214; Giardia CT Table for Chloramine 2: 356; Giardia CT Table for Chloramine 3: 497; Giardia CT Table for Chloramine 4: 0
UV Dose Table
log Category |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 0
|  | 0.5-log | 1-log | 1.5-log | 2-log | 2.5-log | 3-log | 3.5-log | 4-log | 0-log
Virus | 1 | 39 | 58 | 79 | 100 | 121 | 143 | 163 | 186 | 0
Giardia | 2 | 1.5 | 2.1 | 3 | 5.2 | 7.7 | 11 | 15 | 22 | 0
Crypto | 3 | 1.6 | 2.5 | 3.9 | 5.8 | 8.5 | 12 | 15 | 22 | 0
Microcystin | Temp
CT table | oC | UV Dose Table 1: CT mg/l*min
Free Cl2 | Column | 1-0 | 1-1 | 1-2 | 1-3 | 2-0 | 2-1 | 2-2 | 2-3 | 3-0 | 3-1 | 3-2 | 3-3 | 4-0 | 4-1 | 4-2 | 4-3
Row | ug/l | 0 | 10 | 50 | 100 | 0 | 10 | 50 | 100 | 0 | 10 | 50 | 100 | 0 | 10 | 50 | 100
1 | 10 | 22.6 | 27.4 | 46.6 | 70.6 | 32.825 | 39.8 | 67.7 | 102.575 | 91.1 | 110.3 | 187.1 | 283.1 | 299.825 | 363.3 | 617.2 | 934.575
2 | 15 | 19.45 | 23.6 | 40.2 | 60.95 | 28.4 | 34.4 | 58.4 | 88.4 | 78.3 | 94.9 | 161.3 | 244.3 | 255.5 | 309.6 | 526 | 796.5
3 | 20 | 16.925 | 20.5 | 34.8 | 52.675 | 24.6 | 29.8 | 50.6 | 76.6 | 67.925 | 82.3 | 139.8 | 211.675 | 222.6 | 269.8 | 458.6 | 694.6
4 | 25 | 14.675 | 17.8 | 30.3 | 45.925 | 21.375 | 25.9 | 44 | 66.625 | 58.425 | 71.1 | 121.8 | 185.175 | 193.85 | 234.9 | 399.1 | 604.35
|  | pH <=6 |  |  |  | pH =7 |  |  |  | pH =8 |  |  |  | pH =9